## Non Human Comfort- Above Ground
Opteon™ XL Refrigerant Charge Calculator
Enter the Location, Access Categories and Refrigerant using the drop down list. Type in the room dimensions and estimated refrigerant charge.
(Always refer to the full EN 378 standard to ensure all the necessary requirements are fulfilled)
Compressors in machinery room or open air If all compressors and pressure vessels are either located in a machinery room or in the open air then the requirements for a class II location shall apply unless the system complies with the requirements of class III. Coils and pipework including valves may be located in an occupied space.
Location Classification: |  | Class II
Examples:
Access Category: |  | c | Rooms, parts of buildings, buildings where only authorized persons have access, who are acquainted with general and special safety precautions of the establishment and where manufacturing, processing or storage of material or products take place |  |  | Manufacturing facilities, e.g. for chemicals, food, beverage, ice, ice-cream, refineries, cold stores, dairies, abattoirs, non-public areas in supermarkets
| Access Sub-Category: | Other Applications
| Refrigerant: | Opteon™ XL40 | (R454A, GWP¹ = 239)
Room Dimensions / m |  | Height: | 2 | Length: | 5
|  | Width: | 5 | Room Volume: | 50
|  | Estimated Required Refrigerant Charge / kg: | 2.5
Refrigerant Charge Limits / kg
| EN 378 Appendix C1: | 2.78
Systems where the rated cooling (heating) capacity of the indoor unit is not more than 25 % of the total cooling (heating) capacity of the outdoor unit systems and where pipes serving equipment in the occupied space in question are not oversized relative to the capacity of that equipment, where the heat exchanger in the indoor unit and the control of the system are designed to prevent damage due to ice formation, where the refrigerant-containing parts of the indoor unit are protected against fan breakage or the fan is designed to prevent breakage, systems where only permanent joints are used in the occupied space in question except for site-made joints directly connecting the indoor unit to the piping,where the refrigerant-containing pipes in the occupied space in question are installed in such way that it is protected against accidental damage in accordance with FprEN 378-2:2016, 6.2.3.3.4 and FprEN 378-3:2016, 6.2, alternative provisions to ensure safety are provided in accordance with C.3.2.2 and C.3.2.3, doors of the occupied space are not tight-fitting and the effect of flow down is mitigated in accordance with C.3.2.4.
| EN 378 Appendix C3 (QLMV): | 3
| EN 378 Appendix C3 (QLAV): | 6.5
1. GWP values are from Intergovernmental Panel for Climate Change (IPCC) Assessment Report 4 as specified in EU 517/2014 legislation.
Note: The information provided is intended only as a guide and should not be taken in isolation. All assessments should be made with reference to the full text contained within the current EN 378 standard.
DISCLAIMER The information provided herein is believed to be accurate, but is not warranted nor is it intended to be used without independent verification. Because it is provided gratis, the reader assumes sole responsibility for any results obtained in reliance on this information. Statements or suggestions concerning possible use of our products are made without representation or warranty that any such use is free of patent infringement, and are not recommendations to infringe any patent. The user should not assume that all safety measures are indicated, or that other measures may not be required.
Note on E21: The refrigerant charge mass predicted for this application.

## Fluids (hidden)
Fluid | LFL | m1 | m2a | m3b | QLMV | QLAV |  |  |  | Fluid | LFL | m1 | m2a | m3b
Opteon™ XL10 | 0.289 | 1.734 | 7.514 | 37.57 | 0.06 | 0.14 | (R1234yf, GWP¹ = 4) |  |  | Opteon™ XL10 | 0.289 | 0.50113 | 7.514 | 37.57
Opteon™ XL20 | 0.293 | 1.758 | 7.618 | 38.09 | 0.06 | 0.14 | (R454C, GWP¹ = 148) |  |  | Opteon™ XL20 | 0.293 | 0.51509 | 7.618 | 38.09
Opteon™ XL40 | 0.278 | 1.668 | 7.228 | 36.14 | 0.06 | 0.13 | (R454A, GWP¹ = 239) |  |  | Opteon™ XL40 | 0.278 | 0.4637 | 7.228 | 36.14
Opteon™ XL41 | 0.303 | 1.818 | 7.878 | 39.39 | 0.06 | 0.15 | (R454B, GWP¹ = 466) |  |  | Opteon™ XL41 | 0.303 | 0.55085 | 7.878 | 39.39
Opteon™ XL55 | 0.31 | 1.86 | 8.06 | 40.3 | 0.06 | 0.15 | (R452B, GWP¹ = 698) |  |  | Opteon™ XL55 | 0.31 | 0.5766 | 8.06 | 40.3
R32 | 0.307 | 1.842 | 7.982 | 39.91 | 0.063 | 0.15 |  |  |  | R32 | 0.307 | 0.56549 | 7.982 | 39.91
R290 | 0.0375 | 4
R152a | 0.13 | 4
a | Rooms, parts of buildings, building where — sleeping facilities are provided, people are restricted in their movement, — an uncontrolled number of people are present, any person has access without being personally acquainted with the necessary safety precautions | [7 empty] | Hospitals, courts or prisons, theatres, supermarkets, schools, lecture halls, public transport termini, hotels, dwellings, restaurants
b | Rooms, parts of buildings, buildings where only a limited number of people may be assembled, some being necessarily acquainted with the general safety precautions of the establishment | [7 empty] | Business or professional offices, laboratories, places for general manufacturing and where people work
c | Rooms, parts of buildings, buildings where only authorized persons have access, who are acquainted with general and special safety precautions of the establishment and where manufacturing, processing or storage of material or products take place | [7 empty] | Manufacturing facilities, e.g. for chemicals, food, beverage, ice, ice-cream, refineries, cold stores, dairies, abattoirs, non-public areas in supermarkets
Class I | Mechanical equipment located within the occupied space If the refrigerating system or refrigerant-containing parts are located in the occupied space, then the system is considered to be of class I unless the system complies with the requirements of class II. | [6 empty] | I
Class II | Compressors in machinery room or open air If all compressors and pressure vessels are either located in a machinery room or in the open air then the requirements for a class II location shall apply unless the system complies with the requirements of class III. Coils and pipework including valves may be located in an occupied space. | [6 empty] | II
Class III | Machinery room or open air If all refrigerant-containing parts are located in a machinery room or open air then the requirements for a class III location shall apply. The machinery room shall fulfil the requirements of FprEN 378-3. | [6 empty] | III
Class IV | Ventilated enclosure If all refrigerant-containing parts are located in a ventilated enclosure then the requirements for a class IV location shall apply. The ventilated enclosure shall fulfil the requirements of FprEN 378-2 and FprEN 378-3. | [6 empty] | IV
Human Comfort
Other Applications
<1 Person per 10m²
Location | Access Category
II | OA | c | OAcII | NS

## Calculations (hidden)
| 2 | 3 | 4 | 5 |  | 6 | 7
Room size / m3 | Floor Area | QL Calculation Room Size / m³
50 | 25 | 50
Refrigerant | LFL | m1 | m2a | m3b | 20% LFL x RV | QLMV | QLAV | OAaIC1 | OAaIQLMV | OAaIQLAV | OAaIIC1 | OAaIIQLMV | OAaIIQLAV | OAbIC1 | OAbIQLMV | OAbIQLAV | OAbIIC1 | OAbIIQLMV | OAbIIQLAV | OAcIC1 | OAcIQLMV | OAcIQLAV | OAcIIC1 | OAcIIQLMV | OAcIIQLAV | LOcIC1 | LOcIQLMV | LOcIQLAV | LOcIIC1 | aIII | bIII | cIII | aIV | bIV | cIV
Opteon™ XL40 | 0.278 | 1.668 | 7.228 | 36.14 | 2.78 | 0.06 | 0.13 | 2.78 | 2.78 | 2.78 | 2.78 | 3 | 6.5 | 2.78 | 2.78 | 2.78 | 2.78 | 3 | 6.5 | 2.78 | 2.78 | 2.78 | 2.78 | 3 | 6.5 | 2.78 | 2.78 | 2.78 | No Charge Restriction | No Charge Restriction | No Charge Restriction | No Charge Restriction | 54.21 | 54.21 | 54.21
[8 empty] | 2.78 | 2.78 | 2.78 | 2.78 | 3 | 6.5 | 2.78 | 2.78 | 2.78 | 2.78 | 3 | 6.5 | 2.78 | 2.78 | 2.78 | 2.78 | 3 | 6.5 | 2.78 | 2.78 | 2.78 | No Charge Restriction |  |  |  | 54.21 | 54.21 | 54.21